JOINT BASE LEWIS-McCHORD DESIGN STANDARDS

 DIVISION 05 - METALS SECTION 05 05 23.16 STRUCTURAL WELDING

# 07/18

1. GENERAL
	1. REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

AMERICAN INSTITUTE OF STEEL CONSTRUCTION (AISC)

AISC 360 (2016) Specification for Structural Steel Buildings

AMERICAN SOCIETY FOR NONDESTRUCTIVE TESTING (ASNT)

ANSI/ASNT CP-189 (2016) ASNT Standard for Qualification and Certification of Nondestructive Testing Personnel (ANSI/ASNT CP-105-2006)

AMERICAN WELDING SOCIETY (AWS)

AWS A2.4 (2012) Standard Symbols for Welding, Brazing and Nondestructive Examination

AWS D1.1/D1.1M (2015; Errata 1 2015; Errata 2 2016)

Structural Welding Code - Steel

AWS D1.3/D1.3M (2018) Structural Welding Code - Sheet Steel

AWS D1.4/D1.4M (2011) Structural Welding Code - Reinforcing Steel

AWS D1.8/D1.8M (2009) Structural Welding Code—Seismic Supplement

AWS D14.4/D14.4M (2012) Specification for Welded Joints for Machinery and Equipment

AWS Z49.1 (2012) Safety in Welding and Cutting and

Allied Processes ASTM INTERNATIONAL (ASTM)

ASTM E165/E165M (2012) Standard Practice for Liquid Penetrant Examination for General Industry

ASTM E709 (2015) Standard Guide for Magnetic Particle Examination

* 1. SUBMITTALS

Government approval is required for submittals with a "G" designation; submittals not having a "G" designation are for [Contractor Quality Control approval.] [information only. When used, a designation following the "G" designation identifies the office that will review the submittal for the Government.] Submittals with an "S" are for inclusion in the Sustainability eNotebook, in conformance to Section 01 33 29 SUSTAINABILITY REPORTING. Submit the following in accordance with Section 01 33 00

SUBMITTAL PROCEDURES:

SD-01 Preconstruction Submittals Welding Quality Assurance Plan

SD-03 Product Data

Welding Procedure Qualifications; G[, [ ]] Welder, Welding Operator, and Tacker Qualification Inspector Qualification

Previous Qualifications Pre-Qualified Procedures

Welding Electrodes and Rods SD-06 Test Reports

Nondestructive Testing SD-07 Certificates

Certified Welding Procedure Specifications (WPS) Certified Brazing Procedure Specifications (BPS) Certified Procedure Qualification Records (PQR) Certified Welder Performance Qualifications (WPQ) Certified Brazer Performance Qualifications (BPQ)

* 1. QUALITY ASSURANCE

Except for pre-qualified (in accordance with AWS D1.1/D1.1M) and previously qualified procedures, each Contractor performing welding must record in detail and qualify the welding procedure specification for any welding procedure followed in the fabrication of weldments. Conform welding procedure qualifications to AWS D1.1/D1.1M and to the specifications in this section. Submit for approval copies of the welding procedure specification and the results of the procedure qualification test records for each type of welding which requires procedure qualification and the welder, welding operator, or tacker qualification test records. Approval of any procedure, however, does not relieve the Contractor of the sole responsibility for producing a finished structure meeting all the specified requirements. Submit this information on the forms in Annex M of AWS D1.1/D1.1M. Individually identify and clearly reference on the detail drawings and erection drawings all welding procedure specifications, or suitably key them to the contract drawings. In case of conflict between this specification and AWS D1.1/D1.1M, this specification governs.

* + 1. General Requirements

Fabricate work in an AISC Certified Fabrication Plant, Category Standard or as indicated. Work must be erected by an AISC Certified Erector, Category ASCE.

* + - 1. For Structural Projects, provide documentation of the following:
				1. Component Thickness 3 mm 1/8 inch and greater: Qualification documents WPS, PQR, and WPQ in accordance with AWS D1.1/D1.1M and AWS D1.8/D1.8M.
				2. Component Thickness Less than 3 mm 1/8 inch: Qualification

documents WPS, PQR, and WPQ in accordance with AWS D1.3/D1.3M.

* + - * 1. Reinforcing Steel: Qualification documents WPS, PWR, and WPQ in accordance with AWS D1.4/D1.4M.
			1. For other applications, provide documentation of the following:
				1. Submit two copies of the Certified Welding Procedure Specifications (WPS), Certified Brazing Procedure Specifications (BPS) and Certified Procedure Qualification Records (PQR) to the Contracting Officer for review and approval.
				2. Submit two copies of the Certified Welder Performance Qualifications (WPQ)and Certified Brazer Performance Qualifications (BPQ) to the Contracting Officer for review and approval within fifteen calendar days prior to any employee welding on the project material.
				3. Machinery: Qualification documents WPS, PQR, and WPQ in accordance with AWS D14.4/D14.4M.
		1. Previous Qualifications

Welding procedures previously qualified by test may be accepted for this contract without re-qualification, upon receipt of the test results, if the following conditions are met:

* + - 1. Testing was performed by an approved testing laboratory, technical consultant, or the Contractor's approved quality control organization.
			2. The qualified welding procedure conforms to the requirements of this specification and is applicable to welding conditions encountered under this contract.
			3. The welder, welding operator, and tacker qualification tests conform to the requirements of this specification and are applicable to welding conditions encountered under this contract.
		1. Pre-qualified Procedures

Welding procedures which are considered pre-qualified as specified in

AWS D1.1/D1.1M will be accepted without further qualification. Submit for approval a listing or an annotated drawing to indicate the joints not

pre-qualified. Procedure qualification is mandatory for these joints.

* + 1. Retests

If welding procedure fails to meet the requirements of AWS D1.1/D1.1M, revise and re-qualify the procedure specification, or at the Contractor's option, welding procedure may be retested in accordance with AWS D1.1/D1.1M. If the welding procedure is qualified through retesting, submit all test results, including those of test welds that failed to meet the

requirements, with the welding procedure.

* + 1. Welder, Welding Operator, and Tacker Qualification

Each welder, welding operator, and tacker assigned to work on this contract must be qualified in accordance with the applicable requirements of

AWS D1.1/D1.1M, AWS D1.8/D1.8M and as specified in this section. Welders, welding operators, and tackers who make acceptable procedure qualification test welds will be considered qualified for the welding procedure used.

* + - 1. Previous Personnel Qualifications

At the discretion of the Contracting Officer, welders, welding operators, and tackers qualified by test within the previous 6 months may be accepted for this contract without re-qualification if all the following conditions are met:

* + - * 1. Copies of the welding procedure specifications, the procedure qualification test records, and the welder, welding operator, and tacker qualification test records are submitted and approved in accordance with the specified requirements for detail drawings.
				2. Testing was performed by an approved testing laboratory, technical consultant, or the Contractor's approved quality control organization.
				3. The previously qualified welding procedure conforms to the requirements of this specification and is applicable to welding conditions encountered under this contract.
				4. The welder, welding operator, and tacker qualification tests conform to the requirements of this specification and are applicable to welding conditions encountered under this contract.
			1. Certificates

Before assigning any welder, welding operator, or tacker to work under this contract, submit the names of the welders, welding operators, and tackers to be employed, and certification that each individual is qualified as specified. State in the certification the type of welding and positions for which the welder, welding operator, or tacker is qualified, the code and procedure under which the individual is qualified, the date qualified, and the name of the firm and person certifying the qualification tests.

Keep the certification current, on file, and furnish 3 copies.

* + - 1. Renewal of Qualification

Re-qualification of a welder or welding operator is required under any of the following conditions:

* + - * 1. It has been more than 6 months since the welder or welding operator has used the specific welding process for which he is qualified.
				2. There is specific reason to question the welder or welding operator's ability to make welds that meet the requirements of these

specifications.

* + - * 1. The welder or welding operator was qualified by an employer other than those firms performing work under this contract, and a qualification test has not been taken within the past 12 months. Submit as evidence of conformance all records showing periods of employment, name of employer where welder, or welding operator, was last employed, and the process for which qualified.
				2. A tacker who passes the qualification test is considered eligible to perform tack welding indefinitely in the positions and with the processes for which he/she is qualified, unless there is some specific reason to question the tacker's ability. In such a case, the tacker is required to pass the prescribed tack welding test.
		1. Inspector Qualification

Submit inspector qualifications that are in accordance with AWS D1.1/D1.1M and AWS D1.8/D1.8M. Qualify all nondestructive testing personnel in accordance with the requirements of ANSI/ASNT CP-189 for Levels I or II in the applicable nondestructive testing method. The inspector may be supported by assistant welding inspectors who are not qualified to

AWS D1.1/D1.1M, and assistant inspectors may perform specific inspection functions under the supervision of the qualified inspector, as allowed by AWS D1.1/D1.1M.

* + 1. Symbols and Safety

Use symbols in accordance with AWS A2.4, unless otherwise indicated. Follow safe welding practices and safety precautions during welding in conformance with AWS Z49.1.

PART 2 PRODUCTS

* 1. SYSTEM DESCRIPTION

Conform the design of welded connections to AISC 360, unless otherwise indicated or specified. Material with welds will not be accepted unless the welding is specified or indicated on the drawings or otherwise approved. Perform welding as specified in this section, except where additional requirements are shown on the drawings or are specified in other sections. Do not commence welding until welding procedures, inspectors, nondestructive testing personnel, welders, welding operators, and tackers have been qualified and the submittals approved by the Contracting

Officer. Perform all testing at or near the work site. Maintain records of the test results obtained in welding procedure, welder, welding operator, and tacker performance qualifications.

2.1.1 Pre-erection Conference

Hold a pre-erection conference prior to the start of the field welding, to bring all affected parties together and to gain a naturally clear understanding of the project and the Welding Procedure Specifications (WPS) submitted for all welding, including welding done using pre-qualified procedures. Mandatory attendance is required by all Contractor's welding production and inspection personnel and appropriate Government personnel.

Include as items for discussion: responsibilities of various parties; welding procedures and processes to be followed; welding sequence both within a joint and joint sequence within the building; inspection requirements and procedures, both visual and nondestructive testing; welding schedule; and other items deemed necessary by the attendees.

* 1. WELDING EQUIPMENT AND MATERIALS

Provide all welding equipment, welding electrodes and rods, welding wire, and fluxes capable of producing satisfactory welds when used by a qualified welder or welding operator performing qualified welding procedures. Use

welding electrodes. Perform welding using the indicated process. Provide welding equipment and materials that comply with the applicable requirements of AWS D1.1/D1.1M and AWS D1.8/D1.8M. Submit product data on welding electrodes and rods.

PART 3 EXECUTION

* 1. WELDING OPERATIONS
		1. Requirements

Conform workmanship and techniques for welded construction to the requirements of AWS D1.1/D1.1M, AWS D1.8/D1.8M and AISC 360. When

AWS D1.1/D1.1M, AWS D1.8/D1.8M and the AISC 360 specification conflict, the requirements of AWS D1.1/D1.1M govern.

* + 1. Identification

Identify all welds in one of the following ways:

* + - 1. Submit written records to indicate the location of welds made by each welder, welding operator, or tacker.
			2. Identify all work performed by each welder, welding operator, or tacker with an assigned number, letter, or symbol to identify welds made by that individual. The Contracting Officer may require welders, welding operators, and tackers to apply their symbol next to the weld by means of rubber stamp, felt-tipped marker with waterproof ink, or other methods that do not cause an indentation in the metal. Place the identification mark for seam welds adjacent to the weld at 1 m 3 foot intervals. Identification with die stamps or electric etchers is not allowed.
	1. QUALITY CONTROL

Perform testing using an approved inspection or testing laboratory or technical consultant; or if approved, the Contractor's inspection and testing personnel may be used instead of the commercial inspection or testing laboratory or technical consultant. Perform visual or ultrasonic, or dye penetrant inspections to determine conformance with paragraph STANDARDS OF ACCEPTANCE. Conform procedures and techniques for inspection with applicable requirements of AWS D1.1/D1.1M, AWS D1.8/D1.8M, ASTM E165/E165M, and ASTM E709. Submit a Welding Quality Assurance Plan and records of tests and inspections.

* 1. STANDARDS OF ACCEPTANCE

Conform dimensional tolerances for welded construction, details of welds, and quality of welds with the applicable requirements of AWS D1.1/D1.1M, AWS D1.8/D1.8M and the contract drawings. Perform nondestructive testing by visual inspection or ultrasonic, or dye penetrant methods. The minimum extent of nondestructive testing must be random fifty percent of welds or joints, as indicated on the drawings. Submit all records of nondestructive testing.

* + 1. Nondestructive Testing

The welding is subject to inspection and tests in the mill, shop, and field. Inspection and tests in the mill or shop do not relieve the Contractor of the responsibility to furnish weldments of satisfactory quality. When materials or workmanship do not conform to the specification requirements, the Government reserves the right to reject material or workmanship or both at any time before final acceptance of the structure containing the weldment. Any indication of a defect is regarded as a defect, unless re-evaluation by nondestructive methods or by surface conditioning shows that no unacceptable defect is present. Submit all records of nondestructive testing in accordance with paragraph STANDARDS OF ACCEPTANCE.

* + 1. Destructive Tests

Make all repairs when metallographic specimens are removed from any part of a structure. Employ only qualified welders or welding operators, and use the proper joints and welding procedures, including peening or heat treatment if required, to develop the full strength of the members and joints cut and to relieve residual stress.

* 1. GOVERNMENT INSPECTION AND TESTING

In addition to the inspection and tests performed by the Contractor for quality control, the Government will perform inspection and testing for acceptance to the extent determined by the Contracting Officer. The costs of such inspection and testing will be borne by the Contractor if unsatisfactory welds are discovered, or by the Government if the welds are satisfactory. The work may be performed by the Government's own forces or under a separate contract for inspection and testing. The Government reserves the right to perform supplemental nondestructive and destructive tests to determine compliance with paragraph STANDARDS OF ACCEPTANCE.

* 1. CORRECTIONS AND REPAIRS

If inspection or testing indicates defects in the weld joints, repair defective welds using a qualified welder or welding operator as applicable. Conduct corrections in accordance with the requirements of AWS D1.1/D1.1M, AWS D1.8/D1.8M and the specifications. Repair all defects in accordance with the approved procedures. Repair defects

discovered between passes before additional weld material is deposited. Wherever a defect is removed and repair by welding is not required, blend the affected area into the surrounding surface to eliminate sharp notches, crevices, or corners. After a defect is thought to have been removed, and before re-welding, examine the area by suitable methods to ensure that the defect has been eliminated. Repaired welds must meet the inspection requirements for the original welds.

-- End of Section --